To,

The deputy director town planning (DDTP),

Vasai- Virar City Municipal Corporation,

Virar West, Dist: -Palghar, Pin: - 401303.

Subject: - Engineering Report for Development Permission for a proposed Residential and Shopline building on land bearing S.No.125/128, Plot No.18 of Village: Nilemore, Tal: Vasai, Dist.: Palghar. Under EWS LIG Scheme.

REF: SOFTECH PROPOSAL CODE - (VVCMCB/7004/2025/0135/AutoDCR)

Respected Sir,

With reference to above, on behalf of our client: - M/S. Shreeram Enterprises Through Proprietor Mr. Chirag Pravin Raut

(Developers) we hereby submit as follows:

1.	Land Cost				867.00 sq.m X Rs.18600/- per sq.m

Rs. 1,61,26,200.

2.	Construction Cost			3552.18 sq.m X Rs 24,200 per sq.m.

Rs. 8,62,21,454.

Total Cost				= Rs. 10,23,47,654.

(In words Ten Crore Twenty-three Lakhs Forty-Seven Thousand and Six Hundred Fifty-Four).

On basis of available records and considering the current market rate, we hereby confirm that the cost of the said project is less than Rs. 50,00,00,000/- (Fifty Crore), hence provisions of MPCB & MOEF are not applicable to this project.

Thanking You,

Yours faithfully.

To,

The deputy director town planning (DDTP),

Vasai- Virar City Municipal Corporation,

Virar West, Dist: -Palghar, Pin: - 401303.

Subject: - Engineering Report for Development Permission for a proposed Residential and Shopline building on land bearing S.No.125/128, Plot No.18 of Village: Nilemore, Tal: Vasai, Dist.: Palghar. Under EWS LIG Scheme.

REF: SOFTECH PROPOSAL CODE – (VVCMCB/7004/2025/0135/AUTODCR)

Respected sir,

This has reference to our application M/S. Shreeram Enterprises Through Proprietor Mr. Chirag Pravin Raut (Developers) for Engineering Report submitted with your department regarding Development Permission for a proposed Residential and Shopline building on land bearing S.No.125/128, Plot No.18 of Village: Nilemore, Tal: Vasai, Dist.: Palghar. Under EWS LIG Scheme. Now, we are requesting you to please scrutinize the case and grant us the required sanctions at your earliest.

Thanking You,

Yours faithfully.

Subject:-Scrutiny of Engineering Report for Development Permission for a proposed Residential and Shopline building on land bearing S.No.125/128, Plot No.18 of Village: Nilemore, Tal: Vasai, Dist.: Palghar. Under EWS LIG Scheme.

As per the guidelines issued by VVCMC in respect of the Engineer Report, the scrutiny of S.W. Drainage system, water supply [O.H. & U.G Tank], Rain Water Harvesting, Septic Tank for sewage is completed as follows:

1] Storm water Drain Design: The said Architect has submitted the S.W.D. Design Placed at C/    is again reproduced as follows: demarcated on plan as A-B-C  & X-Y-Z.

Q=C I A/3600		C=0.92

I=0.1578 m/hrs

A=(867.00 X 5times = 4335)	Proposed = 4350 sq.mts

Q=0.92x0.1578x4350/3600

Q=0.175 m3/s.

Now, k=Q/√1/s

For 1:600 slope √1/s=0. 201

Ka = 0.175/0.0408	= 4.28

For KP =1.96		=s c/s 0.30m x 0.30m.

QP = KP √1/s		=4.28 x 0.0408

= 0.174 m3/s.> Q

Hence SWD of 0.60m x 0.60m c/s is proposed along the roadside marked in site plan.

Check V = Q/bd		= 0.175 /0.30x0.45 (Add 0.20 Free Board).

=0.2625 m/second

0.6<0.262< 3

For calculation of S.W. Discharge, the Manning’s formula and the constant adopted by the Architect in designing S.W.Drain is as per the guideline issued by VVCMC and it is found in order.

2)    DESIGN OF U.G.TANK

Total built-up area -   3562.87 sq.m.

NO. of people considered = 343.

Water capacity considered for one person =135 Lit for Residential & 45 Lit. Commercial.

Now water required in liter /day =16 persons X 45 Lit. + 315 persons x 135

=34685 Lit. /day required at 75% on total water Required.

= 36480 Lit/day/per Bldg tank proposed capacity.

Proposed U.G Tank

Length =7.60.

Breadth =1.60.

Depth    =3.00 (add 0.30 m space for freeboard).

3) SEPTIK TANK DESIGN / BLDG

No. of persons = 331

Liquid capacity required for 5 people = 1.18 cu.m. (AS per chart, for recommended

interval of cleaning of two years)

So, 331 people capacity required= 0.236 X 331 = 78116 Lit Required

= 81000 Lit Proposed.

Size of Septic tank

Length = 15.00m

Breadth= 1.80m

Depth   = 3.00m(ADD 0.30m space for freeboard).

4)  SOAK PIT DESIGN / BLDG.

Soak pit area = 331 x 135 lit/person x 0.80/water

600 Absorption of soil per m3

= 36996 / 600 = 6166 Lit (Required)

Provided = 8000 Lit.

Size of Soak pit

Length = 2.00m

Breadth= 2.00m

Depth   = 2.00m(ADD 0.30m space for freeboard).

WATER SUPPLY{Overhead and Underground Tanks}

Per Capita Water Requirement of Various Occupancies/ Uses is referred in Appendix – XIV From page No. 126 of D. C. Rule 2001for VVCMC.

| SR.No | Type of Occupancy | Consumption in Liters per capita per day (Lpcd) |
| --- | --- | --- |
| 1 | COMMERCIAL | 45 LITS/PER/DAY |
| 2 | RESIDENTIAL | 135 LITS/PER/DAY |

The above table is referred for consumption of water for residential purpose and the Architect while preparing the following statement of sanitation has taken the same.

SANITATION STATEMENT PHASE (I)

|  | (A) | (B) | (C) | (D) | (E) | (F) | (G) | (H) | (I) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BLDG NO. | BUA | Tenaments | NO OF PER- SONS | WATER REQUI- RED IN LIT/PERS As per D.C. Rule | WATER REQUI-RED SHIFT IN LIT/DAY | SEWAGE DIS- CHARGE (80%) | SEPTIC TANK CAPACITY | O.H. TANK CAPA CITY (LIT) 50% | U.G. TANK CAPA CITY (LIT) 75% |
| BLDG (Gr + ST + 7PT) | 3552.18. Sq.m | 8 Shops & 63 Flats | 331 Nos. | 45 Lit & 135 Lit | 46245 Lit | 36996 Lit | 78116 Lit (Required) 81000 Lit (proposed) Each Bldg (15.00X1.80 X3.00) | 23125 Lit (Required) 27000 Lit (proposed) Each Bldg (4.50X3.00 X2.00) | 34685 Lit (Required) 36480 Lit (proposed) Each bldg (7.60X1.60 X3.00) |

The above table shows capacity/size of over head/under ground tank considered and also indicates the sewage discharge/size of the septic tank.

The Sizes of Septic Tanks as per I.S. 2470 (Part – I) 1963

| No. of Users | Length meter | Breadth B Meter | Liquid Depth D Min. Meter | Liquid Capacity to be provided m3 | Free Board Min. cm. | Sludge to be removed m3 | Recomm- ended Interval of Cleaning |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| 5 | 1.5 | 0.75 | 1.0 | 1.12 | 30 | 0.18 | 6 Months |
|  |  |  | 1.0 | 1.12 | 30 | 0.36 | 1 Year |
|  |  |  | 1.05 | 1.18 | 30 | 0.72 | 2 Years |
| 10 | 2 | 0.9 | 1.0 | 1.8 | 30 | 0.36 | 6 Months |
|  |  |  | 0.0 | 1.8 | 30 | 0.72 | 1 Year |
|  |  |  | 1.4 | 2.52 | 30 | 1.44 | 2 Years |
| 15 | 2 | 0.9 | 1.0 | 1.8 | 30 | 0.54 | 6 Months |
|  |  |  | 1.3 | 2.34 | 30 | 1.08 | 1 Year |
|  |  |  | 1.8 | 3.6 | 30 | 2.16 | 2 Years |
| 20 | 2.3 | 1.1 | 1.0 | 2.53 | 30 | 0.72 | 6 Months |
|  |  |  | 1.3 | 3.3 | 30 | 1.44 | 1 Year |
|  |  |  | 1.8 | 4.55 | 30 | 2.88 | 2 Years |
| 50 | 4 | 1.4 | 1.0 | 5.6 | 30 | 1.8 | 6 Months |
|  |  |  | 1.3 | 7.28 | 30 | 3.6 | 1 Year |
|  |  |  | 2.0 | 11.2 | 30 | 7.2 | 2 Years |

Referring to above table, if we consider the column of 5 year, the capacity of and the size shown in the table seems to be in order.

ENGINEERING REPORT

| SR. NO. | Details Required |  | Remarks |
| --- | --- | --- | --- |
| 1 | i) ii) iii) iv) v) vi) a) b) vii) viii) ix) x) | SOFTECH PROPOSAL CODE Name of Architect Name of the Developers Area / S. No. D.P. Sheet No. ( 1:10,000 ) Date of site inspection by Deputy Director Town Planning Junior Engineer What is the totals gross area of the plot (Sq. Mtrs.) How many number of person considered in the project. What is the quantity of discharge of sewage (in liters)? What is the investment in the total project (Rs. In Corers) | (VVCMCB/7004/2025/0135/AutoDCR) L.E. Mufaddal Merchant M/S. Shreeram Enterprises Through Proprietor Mr. Chirag Pravin Raut S.No.125/128, Plot No.18 of Village: Nilemore, Sheet No. 867.00 sq. m 331 Persons 36996 Lit 10,23,47,654.Cr |
|  | The above details as (iv) to (X) shall be for the total project and not for the phases or parts. If the |  |  |
|  | i) ii) iii) | Number of person are 1000 or above OR Discharge of sewage is 50,000 liters per day or above. OR The investment is Rs. 50 Crores or above. Then the whether the clearance from the Ministry of Environment & Forest. Govt. of India has been obtained? If yes, whether the copy of the clearance is enclosed? | --No— --No— Not required |

| 2 | The plot level shown in the plan Whether it is (-) 45 m GIS or 300 mm above the finish level If yes, what is the proposed plinth level. | 2.900MRL To 3.300 MRL |
| --- | --- | --- |
| 3 | Finished plot level shown in the plan (in GST). | 3.300 MRL |
| 4 | The proposed plinth level shown in the plan Whether it is 600 mm above the finished plot level If yes what is the proposed plinth level | 3.900 MRL |
| 5 | Whether the storm water drainage system has been designed as per the norms adopted by VVCMC for the rainfall intensity of 15.87 cms/houre If Yes - Whether the discharge of the storm water is in the system approved by VVCMC i.e. in open channel/constructed drain etc.+ - What is the starting HFL of the storm water drainage system submitted by the Architect/Developers - What is the discharge HFL of the storm water drainage system submitted by the Architect/Developers - Whether any existing natural flowing stream or channel is passing through the plot If yes, has it been trained properly | --Yes— --Yes— 3.300 M. RL 2.710 M. RL --No— |
| 6 | Roads : - Whether the cross section of the road have been adopted by the Architect/Developers as per the approved standards - Whether the ground improvement is required for the construction of roads - If yes whether the same is submitted with the drawing - The finished road edges shall be 150 mm below the plot level and shall be demarcated property by the providing Kerbstone / water table / foot path whether required. | --Yes— --No— --No— --Yes-- |
| 7 | Water Supply : - Whether the norms for water supply as per DCR have been considered - What is the total population considered? - What is the total capacity required? - What is the total capacity provided in OH tank? - What is the total capacity provided in UG tank? - Is it adequate as per the norms? - Whether the firm commitment letter for water supply from local authority has been submitted. | --Yes— 331 persons 46245 Lit 27000 Lit 36480 Lit --Yes— —No-- |

| 8 | Sewerage Disposal i)Whether the norms as per the general Standard for discharge of Environment Pollutants to be discharged into Inland Surface Water (as amended from time to time) have been adhered while designing the sewerage disposal system? ii)Whether the following desired outlet parameters. Sr.No. Parameter Desired Values 01 PH 6.59 02 Supended solids (TTS <10 ppm 03 Oil and Greases (O & G) < 10 ppm 04 Biological Oxygen Demand (BOD) < 5 ppm 05 Chemical Oxygen Demand (COD) < 50 ppm 06 Total Ammonical Nitrogen (NH3 – N) < 2 ppm 07 Total Phosphorous (TP) < 1ppm | Undertaking Attached The M.P.C.B. norms shall be strictly followed and implemented to achieve parameters of sewage influent and characteristics . |
| --- | --- | --- |
| 9 | Whether the rain water harvesting system is proposed by the Architect / Developers? | Yes |
| 10 | Whether the solar water heating system has been proposed by the Architect / Developers to be installed? If yes, what is the capacity proved? Is this capacity adequate? | NA |
| 11 | Whether the system for disposal of solid waste, dry and wet garbage, and organic waste has been submitted as per the standards? | Yes |
| 12 | Street Lights: Whether the system submitted is for maintaining illumination level of 15 lux : | Yes |
| 13 | Whether the reservation of D.P. Road, C.F.C. and water channel etc. has been demarcated on the plot? | NO |
| 14 | Layout Plan showing the details for the road, S.W. drainage system, sewerage system, rain-harvesting system. Solar heating system street light, solid waste disposal system has been submitted. | Yes |
| 15 | Whether the required design details for the above have been submitted? | Yes |
| 16 | Additional requirement if any as per DCR? | NA |

Recommendation:- Recommended for approval of the engineering Report for SOFTECH PROPOSAL CODE -(VVCMCB/7004/2025/0135/AUTODCR) submitted by the Architect L.E. Mufaddal Merchant

DDTP(Vvcmc)

The following are the conditions proposed to be included in the commencement certificate while granting building permission:

- VVCMC reserves the right to amend or add conditions in respect of Engineering report and the same shall be binding on the application.

- In no case sewage effluent shall find its way to any water body directly/indirectly at any time.

- the owner shall be responsible to discharge water of proposed drain system by connecting to the near by discharge point like natural stream as per sanction D.P. plan, existing drain or municipal drain. Owner shall take all measures as directed , which take care to avoid flooding due to development in proposed layout.

- Discharge of sewage shall confirm to the norms and standards prescribed by Maharashtra State Pollution Control Board.

- there shall no cutting of trees except as per prevailing rules, If required prior approval of competent authority shall be obtained.

- The owner shall give facility to the other adjacent plot owner for efficient disposal of storm water without any condition.

- VVCMC may impose any additional conditions time to time during progress of work ,if necessary.

- Rain water harvesting structure shall be constructed so as not to endanger the stability of building or earth work. The structure should be designed such that no dampness is caused in any part of the wall or foundation of the building or those of adjacent building.

- S. w. drain across the road and at the entry to the plot shall be heavy duty.

DDTP(V.V.C.M.C)

Special Note :-

- In case there is any change in the layout for which this engineering report is granted the planning section to direct the application to obtain revised engineering report before grant of  commencement certificate.

DDTP

(Vasai Virar City Municipal Corporation)

# SITE INSPECTION REPORT

Architect – L.E. Mufaddal Merchant

The said site pertaining to of Village: Nilemore was visited by the undersigned on   /    /   . The gross area of the plot is 867.00 m2 situated on Land Bearing S.No.125/128, Plot No.18 of Village: Nilemore, Tal: Vasai, Dist.: Palghar. Under EWS LIG Scheme. The Net BUA of the plot is 3562.87 sq.m. The access road to this plot existing 9.00m wide existing Municipal Road which is Asphalted. There does not exist natural nallah through the plot.

PHYSICAL SURVEY: The levels of the plot submitted by the Architect placed at Pg. C/…. are checked by the undersigned and is generally found to be correct. These levels are taken by flying levels from existing Culvert Bearing bench mark value of M RL C/….

The following are the existing features of the plot:

1)	a)	Nature of plot	             :	RESIDENTIAL & COMMERCIAL

b)	Plot Levels		 :	Ranges from 2.90m. RL to 3.30 m. RL.

c)	S.W.D. System	             :    	Exist 9.00 m D.P.Road.

d)	Road EdgeLevel	 :	2.550 M.RL.

e)	Proposed Internal	 :	Existing 0.30 m wide.

S.W.D. Scheme

wide road			Proposed  Internal Drain

A) Width	:   0.30  M.RL.

B)  Top level 	:   3.300 M.RL.

C) I.L            	:   2.720 M. RL.

2)	Discharge Point		:	(Proposed Road sidedrain)

A) Drain width: 0.45m.

B) Discharge Top: 2.750 M. RL.

C) Discharge IL  : 1.800 M. RL.

Note:-

- The applicant has proposed (G+ ST +7PT) Residential Bldg.

- The access to the plot is from the existing 9.00 m wide road.

- Proposed plot level 3.300 M.RL. & Proposed plinth level 3.900 M.RL. & Proposed stilt level is 3.450 M.Rl. (Placed at C/….).

- The applicant has to properly construct the  S.W. Drain according to Cross section place c/… and Provide Heavy Duty Slab for the Entry of the plot submitted please.

J.E.(VVCMC)

DDTP (VVCMC)